Reliable Power system stabilizers

H.M. Soliman1          J.H. Taylor 2      A.L. Elshafei1      E.M.K. Makkawy1

- Electrical Engineering Department, Faculty of Engineering, Cairo University, Cairo, Egypt.

2. Electrical & Computer Engineering Department, University of New Brunswick, Fredericton, NB, Canada E3B 5A3.

# Abstract

This paper describes a simple method for the design of reliable decentralized stabilization using two controllers. Excitation and governor controllers are used to stabilize a synchronous machine infinite bus system. The goal is to maintain stability when both controllers act together and when either one of the two controllers fails (i.e., to achieve fault tolerant control).

1-Introduction

Power systems are subjected to low frequency oscillations due to disturbances. Such oscillations may sustain and grow to cause system separation if adequate damping is not available. To enhance system damping, generators are equipped with power system stabilizers (PSSs) that provide supplementary feedback stabilizing signals in the excitation channel.

Conventional PSSs are proposed in [1,2] that act by adding a phase lead controller to the system.  Several approaches based on modern control theory have been applied to the PSS design problem. These include optimal control [3], intelligent control [4,5,6] and robust control [7].

Unfortunately, if an outage occurs in a PSS (excitation control), the synchronous machine (plant) loses stability. Motivated by the idea that “two controllers are better than one” for stabilizing a single plant, it has been found that governor control can be of great help. A control system designed to tolerate failures in system stabilizers while maintaining acceptable closed loop stability is called a reliable control system. In other words, the system should be stable when both excitation and governor controllers are acting together and in the case of the possible outage of either one of the controllers.

It should be pointed out that redundancy is the key ingredient in any reliable control system. It should also be noticed that the fundamental difference between traditional robust control and reliable control lies in the fact that the former mainly deals with medium size parameter variations or model uncertainties, while the latter treats more drastic changes in system configurations caused by outright component failures.

There are two methodologies for reliable control system design, factorization methods [8, 9, 10], and state space methods [11]. Even though reliable control systems are extremely important in practice, unfortunately, only a very limited number of papers are devoted to this subject in the literature.

In this paper a novel method is proposed to design reliable excitation and governor controllers for enhancing power system dynamic stability.

- Problem Formulation

Given a linear time invariant system,

(1)

where x(t)  Rn, u(t)  R2 and y(t)  R2 represent the state, input and output vectors, respectively.

It is desired to stabilize the system in a decentralized manner, i.e., two controllers are used where each controller uses its local outputs only. The assumption of decentralization (independent sensor for each controller) is crucial so as to increase the chance that at least one of the controllers survives. Otherwise, in case of sensors’ failure, both controllers will be disabled and the system will break down. Accordingly, we decompose system (1) as follows:

#### (2)

#### Thus system (1) will be treated as a two-channel linear system,

#### (3)

#### where  and   are two control inputs and   ,   are two measured outputs of the system. We assume that the triples (C1, A, B1) and (C2, A, B2) are both stabilizable and detectable. Therefore the system can be stabilized either from u1 using y1 only or from u2 using   only (decentralized control).

From (3), we obtain the transfer matrix of the system as

(4)

where

(5)

We also use G(s) = [Gi,j (s) ], i,j = 1,2 to represent the transfer matrix of the overall system.  Now we connect two dynamic output feedback controllers

(6)

to the system. R1 and R2 are the reference signals for channels 1 and 2, respectively.  For simplicity, we drop the argument s.

The block diagram of the closed loop decentralized control is as shown in Fig (1).

R1

R2

##### Fig. 1. Reliable decentralized controllers

Failures that occur in sensors (i.e., in matrices C1, C2) and/or actuators (matrices B1 and B2) are modeled in Fig (1) by replacing the transfer functions K1 and/or K 2 by zero.

Our goal is to find reliable controllers that maintain the stability of G with the two controllers acting together and also under the possible failure of either one of the two controllers. We summarize this objective as follows:

Problem: Given the system (3), described in transfer function form as in (4), find K1 and K2 such that:

(i) when K1 is the only active controller, it stabilizes G.

(ii) K2 stabilizes G when K1 is either on (active) or off (failed).

Of course, we could have started with K2 instead of K1. Based on condition (i) and (ii), we may consider K1 to be the main controller and K2  to be a redundant (backup) controller.

3-Problem solution

- Design of K1, when K2  is off

We use the following lemma:

Lemma: When K2 is off, K1 stabilizes the overall system (3) if and only if it stabilizes the subsystem G11.

Proof: when K2 is off, we have

(7)

Designing K1 to stabilize the subsystem G11 via the feedback  U1= R1 - K1 Y1  results in

(8)

Solving (8) for Y, we obtain

(9)

where

(10)

(11)

The form of d((s) proves the result Q.E.D.

- Design of K2

This controller K2  must stabilize the  overall system G when K1 is either on or off. It is easy to show that the characteristic equation of the system is

Hence, we conclude the following two cases.

(	Case 1: K1 is off – As before, K2 stabilizes the overall system G if and only if it stabilizes the subsystem G22.

(	Case 2: K1 is on – In this case we observe that the system seen by K2  is given by  Y = G'R (9). Thus the controller stabilizes (9) if and only if it stabilizes. So,  must stabilize both  and  simultaneously. In other words, the reliable stabilization problem is reduced to a simultaneously stabilization problem [12, 13]. It will be shown that using MATLAB, the root locus technique can be used to accomplish the required design. The proposed algorithm is illustrated using a single-machine infinite-bus model of a power system.

4. Reliable Stabilization of a Single Machine Infinite Bus Model

The objective is to design reliable decentralized excitation and governor controllers to enhance the dynamic stability of a synchronous machine infinite bus model of a power system, Fig. 2.

Fig. 2. Schematic diagram of a single-machine infinite-bus system

Excitation & Governor supplementary control

The studied system is modeled as a fifth order system. A third order synchronous machine is represented by the state variable   (incremental torque angle), (incremental angular velocity), (incremental voltage proportional to q-axis flux linkage, behind transient reactance).In addition, a first order speed regulator is represented by the state variable (incremental mechanical power input), and a first order voltage regulator represented by the state variable (incremental field voltage).

The dynamics of the studied system is described by [2, 14]

(12)

where

(14)

where

and   (0= 314

Remark 1: The above model neglects stator transients and the effects of damper bars. Had the effects of the latter been considered, it will result in more damping than that will be provided by the proposed design.

Remark 2: Selecting the main and back up controllers

Of course, we could have started the design with K2 instead of K1. Based on the condition (i) and (ii), we may consider K1 to be the main controller and K2 to be a redundant (backup) controller. In practice, exciter channel provides rapid control, so it is selected as the main controller. On the other hand, the governor channel provides slow control (due to its time delay), so it is selected as the back up controller.

Using the data in appendix, we get

To stabilize the system in a decentralized manner, it is possible to decompose  and  as follows:

.

It is easy to check that the triples  and  are controllable and observable. The transfer matrix of this system is

(13)

where   .It is to be noticed that  the open-loop system is unstable.  We follow the process in Section 3, starting with the first loop (K1) then designing K2 to solve the simultaneous stabilization problem, see Fig. 2.

a-   Design of  K1 to stabilize G11

Using the root locus technique, we design K1 controller to stabilize G11 (13), The controller transfer function is selected to be

.

The added pole at -50 is selected to be nondominant (having slight effect on the dynamic response) .This achieves a realizable proper transfer function. The designed K1 is nearly PID (Proportional Integral Derivative) control

widely used in industry.

b- Design of K2 to stabilize G22 and G`22 simultaneously

We use the relations in (10). When K1 fails, K2 stabilizes the overall system if and only if it stabilizes G22.  Also, when K1 is on, K2 stabilizes the overall system if and only if it stabilizes G'22. The transfer functions G22 and G'22 are given by

Once again, we use the root locus technique to design  that simultaneously stabilizes G22 and G'22 . The resulting controller transfer function is

.

It is to be noted that K2 is a double lead controller.

The above controllers  and  achieve at least a degree of stability (0.98).

The impulse responses of the systems under reliable stabilization are shown in Figs. 3-5. As designed, the system can tolerate the outage of any of the two controllers without seriously deteriorating the degree of stability.

Fig. 3. Impulse responses when K1 and K2 are active (no failure).

Fig. 4. Impulse responses when K1 only is active (failure in K2)

Fig. 5. Impulse responses when K2 only is active (failure in K1).

5- Robustness evaluation of designed stabilizers ٌ

To assess the effectiveness and robustness of the proposed stabilizers, three different loading conditions are selected as follows

_______________________________

Loading 	P (p.u)		Q (p.u)

_______________________________

Nominal 	1.2		0

Light		0.7		0.3

Heavy		1.2		0.4

______________________________

The reliable stabilizers give similar behavior as shown in Figures 3-5.

The above analysis shows the effectiveness and robustness of the proposed reliable stabilizers and their ability to provide good damping of low frequency oscillations under different loading conditions.

6- Conclusions

A new method has been developed for the design of a reliable excitation/governor control system. The algorithm is applied to a single-machine infinite-bus model. The two controllers retain the stability margin of the system when both controllers are operative and when either one of them fails.

References

1-P.Kundur”Power system stability and control” McGraw Hill, 1994

2-P.M.Anderson and A .A . Fouad "Power system control and stability "IEEE Press, J .Wiley, 2/e, 2003

3-Y.N.Yu”Electric power system dynamics” Academic Press, 1983

4-M.A.Abido and Y .L. Abdel Magid”Hybridized rule based power system stabilizers with genetic algorithms” IEEE Trans. Power system, vol. 14, pp600-7, 1999

5-N.Hosseinzadeh and A. Kalam “A direct adaptive fuzzy power system stabilizer” IEEE Trans. Energy Conversion, vol. 14, pp1564-71, 1999

6-P.Shamsollah and O .P .Malik ”An adaptive power system stabilizer using on line trained neural networks” ibid, vol. 12, pp382-7, 1997

7-H.M.Soliman, A .L .El Shafei, A .A .Shaltout and M .F .Morsi ”Robust power system stabilizer” IEE Proc. – Gen. Trans. Distrib., vol. 147, pp285-91, 2000

8-X.L Tan, D .D .Siljak and M .Ikeda “Reliable stabilization via factorization methods” IEEE Trans., vol. 37, pp1786-90, 1992

9-M.Vidyasagar and N. Viswanadham “Algebraic design techniques for reliable stabilization “IEEE Trans. AC, vol. 27, pp1085-95, 1982

10-A.N.Gundes “Reliable decentralized stabilization of linear systems” IEEE Trans, . AC, vol. 43, pp1733-9, 1998

11-R.J.Veillette”Reliable linear quadratic state feedback control” Automatica , vol. 31, pp 137-43, 1995

12-V.D.Blondel “Simultaneous stabilization of linear systems” Springer Verlag, 1994

13-B.K.Ghosh and X .A .Wang”Sufficient condition for generic simultaneous pole assignment and stabilization of linear MIMO dynamical systems” IEEE AC, vol. 45, pp734-8, 2000

14-H.M.Soliman and M .F .Sakr “Wide range power system pole placer” IEE Proc. , vol. 135 , Pt. C, pp195-201, 1988

Appendix

Studied system data (in p.u. , unless otherwise stated)

Machine constants

Excitation system sec

Governor system sec

Speed regulation

Loading P=1.2, Q=-0.5

# Text boxes

-

-

K1

G

K2

Y1

Y2

U2

_

K2

_

Governor

###### T

Ex

U1

Vt

AVR &

Exciter

Generator

Trans.

Transmission Line

_

K1

Vref

_

Infinite

Bus