Course # (EE6723) Power Quality

Supervisor: Professor: Dr. A.M Sharaf (P.Eng)

By

Pierre Kreidi

Student ID # 205475

ECE Department

University of New Brunswick
CONTENTS
Summary………………………………………………………………………………..4

1. Background………………………………………………………………………… …5     
2. Why Are we concerned about Power Quality…………........................................7
3. Power Quality Issues and Problem Formulation…………………………………...8
4. Total Harmonic Distortion and Power Factor……………………………………….9
5. Power Quality Disturbances………………………………………………………….10
5.1 Short duration voltage variations…………………………………………………..11
5.1.1 Sag…………………………………………………………………………………………11
5.1.2 Swell………………………………………………………………………………………..12
5.1.3 Interruption…………………………………………………………………………..…….13
5.2 Long duration voltage variations………………………………………………..…..13
5.2.1 Overvoltage…………………………………………………………………………….….13
5.2.2 Undervoltage……………………………………………………………………………....14
5.3 Transients……………………………………………………………………………..14
5.3.1 Impulsive Transient……………………………………………………………………….14
5.3.2 Oscillatory Transient………………………………………………………………………14
5.4 Voltage imbalance……………………………………………………………………16
5.5 Waveform distortion…………………………………………………………………..17
5.5.1 DC offset……………………………………………………………………………………17
5.5.2 Harmonic……………………………………………………………………………………17
5.5.3 Interharmonics……………………………………………………………………………..18
5.5.4 Notching……………………………………………………………………………………..19
5.5.5 Noise…………………………………………………………………………………………19
5.6 Voltage Fluctuation……………………………………………………………………19
5.7 Power Frequency variations………………………………………………………...20
6. Reactive Power Problems…………………………..................................................20
6.1 Reactive power sources………………………………………………………………21
6.1.1 Generators…………………………………………………………………………21
6.1.2 Power Transfer Components……………………………………………………22
6.1.2.1 Transformers…………………………………………………………………………..22
6.1.2.2 Transmission Lines and Cables……………………………………………………..23
6.1.2.3 HVDC Converters……………………………………………………………………..24
6.1.3 Loads……………………………………………………………………………….24
6.1.3.1 Induction motors……………………………………………………………………….24
6.1.3.2 Induction generators………………………………………………………………….25
6.1.3.3 Discharge lightning…………………………………………………………………….25
6.1.3.4 Constant energy loads…………………………………………………………..……25
6.1.3.5 Arc furnaces………………………………………………………………………..…..26
6.1.4 Reactive Power Compensation Devices…………………………………..……26
6.1.4.1 Synchronous condensers……………………………………………………..………26
6.1.4.2 Static VAR compensators………………………………………………….…………27
6.1.4.3 Harmonic Filter…………………………………………………………………….…..27
6.1.4.4 Static synchronous compensators………………………………………………….28
6.1.4.5 Series capacitors and reactors……………………………………………………..29
6.1.4.6 Shunt capacitors……………………………………………………………………..29
6.1.4.7 Shunt reactors………………………………………………………………………..30
6.1.5 Why Power factor Correction…………………………………………………..30
6.1.5.1 Power factor correction techniques………………………………………..30
7. Software……………………………………………………………………………….31
8. Digital Simulation Models……………………………………………………………31
8.1 System models…………………………………………………………………...32
8.1.1 Cases # 1 to Case # 5……………………………………………………….33
Case # 1……………………………………………………………………….33

      Case # 2………………………………………………………………………..33

      Case # 3………………………………………………………………………..34

                  Case # 4………………………………………………………………………..34
                  Case # 5………………………………………………………………………..35
References……………………………………………………………………………………………36
Appendix ‘A’…………………………………………………………………………………………..38

Appendix ‘B’…………………………………………………………………………………………..43

Appendix ‘C’…………………………………………………………………………………………..47

Appendix ‘D’…………………………………………………………………………………………..53

Appendix ‘E’…………………………………………………………………………………………..55

Summary
This Project comprises of 5 separate cases of Power Quality, Reactive Power and Modulated Power Filter Compensators. These cases have been modulated with and without compensation devices and have been simulated using both Matlab/Simulink and PSCAD software. 
The 5 cases are as follows:

1. Power Quality Enhancement Using Modulated Power Filter
2. Power Quality Enhancement and Voltage regulation Using Modulated Power Filter

3. Power Quality Enhancement Using STATCOM

4. Power Quality Enhancement addressing the Tingle Voltage Issue

5. Power Quality Enhancement and Voltage regulation Using STATCOM
Detail information about the cases and digital simulation are shown under section 8.1.1 and under the Appendices A to E.
1. Background

The research course project EE6723 addresses the current issues of Electric Power Supply Pollution, Power Quality (PQ) and Harmonic Distortion Problems. The term “Power Quality” is in general a broad concept and is associated with electrical distribution and utilization systems that experience any voltage, current or frequency deviation from normal operation. For ideal electrical systems, the supplied power should have perfect current and voltage sinusoidal waveforms, being safe and reliable. But the reality is that the electric utilities controls the voltage levels and quality but are unable to control the current, since the load profile dictates the shape of the current waveform. Thus, the utility should maintain the bus voltage quality at all times. This simple consideration makes power quality (PQ) equal to voltage quality as shown in Figure 1.1

Defining precisely the Power Quality is a tremendous task; one of the common definitions is:   

Definition 1: “Power quality is a summarizing concept, including different criteria to Judge the technical quality of an electric power delivery”.  Another definition is developed and adopted by Ontario Hydro:

Definition 2: “Power Quality is the degree to which both the utilization and delivery of electric power affects the performance of electric equipment”.

In general there is no unique definition of power quality. The power quality problem can be viewed from two different angles related to each side of the utility meter, namely the Utility and the Consumer. An alternative definition of PQ is adopted: 

Definition 3: “Power quality problem is any power problem manifested in voltage, current, or frequency deviation that results in failure or misoperation of customer equipment”. Power quality can be simply defined as shown in the interaction diagram Figure 1.1 
[image: image30.wmf]Electrical Grid

Utility

Loads

Consumers

Voltage

Quality

Current

Quality

Power

Quality


[image: image31.wmf]Ÿ

Converter Type

Ÿ

Arc Type

Ÿ

Dynamic

Ÿ

Cyclical

Ÿ

Ripple

Ÿ

Inrush

Ÿ

Temporal

Ÿ

Motorized on/off

Nonlinear

Load

N

L

L

R

s

L

s

V

s

V

L

Y

F

(s)

on/off or

PWM

Load Bus

Utility

System+Transformer+Feeder

Electric

Equivalent

(Plant) Load

Switched/Modulated

Power Filter or Static

Capacitor Compensator

 i

s

Control

Signals

Smart

Controller

*

V

s

Ps

SMPF

Nonlinear Load (NLL)

* Smart-controllers are

based on specified control

objectives


Delivering a certain level of voltage stability and sinusoidal quality should be the main concern for designers of the utility electrical grid. When electrical distribution/utilization system is interconnected, electric loads and their profile, grid design, utility operation including the electric load degree of nonlinearity, all together affect and influence the power quality.  

An important article appeared in the Electrical Business Magazine in December 2001 quoted Ms Jane Clemmensen, a well-known power quality authority in Berkerly, California, “as every year, North American industries lose Tens-of-Billions of Dollars in downtime due to electric faults in the quality of electric power delivered to factories and other industrial facilities”.

2. Why Are We Concerned With Power Quality

Power Quality (PQ) has caused a great concern to electric utilities with the growing use of sensitive and susceptive electronic and computing equipment (e.g. personal computers, computer-aided design workstations, uninterruptible power supplies, fax machines, printers, etc) and other nonlinear loads (e.g. fluorescent lighting, adjustable speed drives, heating and lighting control, industrial rectifiers, arc welders, etc).  All nonlinear and time varying temporal type electric loads fall generally in two wide categories, namely the analog arc (inrush/saturation) type and digital converter (power electronic) switching type. The Electric Power Research Institute (EPRI) gives a rough estimation that in 1992, 15 to 20% of the total electric utility load was nonlinear and this trend in rising and is expected to reach 50 to 70% in the year 2000.  

The reasons behind the growing concern about power quality are:

· The characteristics of the electric loads have changed dramatically with the proliferation of new microelectronics and sensitive computer type equipment. 

· Harmonics cause equipment to fail prematurely and also decrease the efficiency of the electric distribution/utilization network. 

· Electric power systems are now interconnected, integrated, and thus any system disturbance can have an extended serious economic impact particularly for large industrial type consumers due to process shutdown. 

· Deregulation of the electricity market. Consumers are now much more aware of the PQ problems issues, and its effect on equipment failure and safety hazards. 
3. Power Quality Issue and Problem Formulation

The rapid change in the electric load profile from being mainly a linear type to greatly nonlinear, has created continued power quality problems which are difficult to detect and is in general complex. The most important contributor to power quality problems is the customers’ (or end-user electric loads) use of sensitive type nonlinear load in all sectors (Industrial, Commercial and Residential). 

Power Quality issues can be roughly broken into a number of sub-categories: 

· Harmonics (integral, sub, super and interharmonics)

· Voltage swells, sags, fluctuations, flicker and Transients

· Voltage magnitude and frequency, voltage imbalance

· Hot grounding loops and ground potential rise (GPR)

· Monitoring and measurement of quasi-dynamic, quasi-static and transient type phenomena. 

Nonlinear type loads contribute to the degradation in the electric supply’s Power Quality through the generation of harmonics. The increased use of nonlinear loads makes the harmonic issue (waveform distortion) a top priority for all equipment manufacturers, users and electric utilities. Severe Power System harmonics are usually the steady state problem not the transient or intermittent type, and these harmonics can be mitigated by using the new family of modulated/switched power filters. 

Lower order harmonics cause the greatest concern in the electrical distribution/utilization system.  Harmonics interfere with sensitive-type electronic communications and networks. Low order triplen harmonics cause hot-neutrals, grounding potential rise (GPR), light flickering, malfunction of computerized data processing equipment and computer networks and computer equipment. 

There are several defined measures commonly used for indicating the harmonic severity and content of a waveform. One of the most common measures is total harmonic distortion in current 
[image: image1.wmf]i

THD

)

(

. 


[image: image2.wmf](

)

ú

ú

ú

ú

ú

û

ù

ê

ê

ê

ê

ê

ë

é

=

å

¥

=

1

2

2

I

I

THD

n

n

i

;

Where 
[image: image3.wmf]1

I

: Fundamental (60Hz) Current; n: Harmonic order and 
[image: image4.wmf]n

I

: Harmonic current.

4. Total Harmonic Distortion (THD) and Power Factor (PF)

The power factor PF for any non-sinusoidal quantities is defined by:


[image: image5.wmf]1

1

1

1

cos

cos

f

f

S

S

S

S

S

S

I

I

I

V

I

V

PF

=

=



[image: image6.wmf]1

S

I


is the rms value of the fundamental 60Hz component of the current. The displacement power factor (DPF, which is the same as the power factor in linear circuits with pure sinusoidal voltage and current) is defined as the cosine of the angle 
[image: image7.wmf]1

f

 (angle between the fundamental-frequency (60Hz) current and voltage waveforms) which could be written as: 
[image: image8.wmf]1

cos

f

=

DPF

, therefore, the power factor PF with a nonsinusoidal current is:


[image: image9.wmf]DPF

I

I

PF

S

S

1

=


In terms of total harmonic current distortion 
[image: image10.wmf]i

THD

)

(

, the PF and 
[image: image11.wmf]S

I

 (the rms value of the total current) could be written as:

[image: image32.emf]powergui

Continuous

Zn

v

+

-

Transformer Bus

A

B

C

a

b

c

Three-Phase Fault

AB

C

AB

C

Scope2

Rg

PWM

Nutral Harmonic 

In

NLL_C

In

N

NLL_B

In

N

NLL_A

In

N

MPFC

s

1

s

2

Cn

AB

C

Load Harmonic 

In

Load Bus

A

B

C

a

b

c

Load 

V

I

Linear  Load

AB

C

[Vn]

Goto

[In]

-

K- [In]

From3

[Vn]

From2

[In] IL

VL

Current Measurement

i

+

-

Controller

In

s1

s2

25kv/600v 

400kVA

A

B

C

a

b

c

n

25 KV AC source

AB

C

1 km Feeder

A

B

C

A

B

C


[image: image12.wmf]DPF

THD

PF

i

2

1

1

+

=


[image: image33.emf]s2

2

s1

1

sigma2 sigma1

rEh

Transfer Fcn2

1

0.001s+1

Saturation

PWM Generator

Signal(s)

Pulses

Irms

signal

rms

I1 ref

0.15

Gama n

1.8

Gama h

1.2

Gama I

0.8

Et

En

Ei

PID

Delay1

Abs

|u|

In

1


        where


[image: image13.wmf](

)

2

1

1

i

S

S

THD

I

I

+

=


From an examination of (4.1) and (4.2), we can conclude that the power factor value decreases with any high current harmonic content or distortion 
[image: image14.wmf]i

THD

)

(

. These definitions assume that the source voltage is near sinusoidal of fundamental frequency (maximum allowable 
[image: image15.wmf]V

THD

)

(

 =5%).

5. Power Quality Disturbances
In an electrical power system, there are various kinds of power quality disturbances. They are classified into categories and their descriptions are important in order to classify measurement results and to describe electromagnetic phenomena, which can cause power quality problems. Some disturbances come from the supply network, whereas others are produced by the load itself. The categories can be classified below
Short-duration voltage variations 

· Long-duration voltage variations 

· Transients 

· Voltage imbalance 

· Waveform distortion 

· Voltage fluctuation 

· Power frequency variations 

5.1   Short-Duration Voltage Variations 
There are three types of short-duration voltage variations, namely, instantaneous, momentary and temporary, depending on its duration. Short-duration voltage variations are caused by fault conditions, energization of large loads, which require high starting currents or loose connections in power wiring. Depending on the fault location and the system conditions, the fault can generate sags, swells or interruptions. The fault condition can be close to or remote from the point of interest. During the actual fault condition, the effect of the voltage is of short-duration variation until protective devices operate to clear the fault. 

5.1.1    Sag 
A sag (also known as dip) is a reduction to between 0.1 and 0.9 pu in rms voltage or current at the power frequency for a short period of time from 0.5 cycles to 1 min. A 10% sag is considered an event during which the RMS voltage decreased by 10% to 0.9 pu. Voltage sags are widely recognized as among the most common and important aspects of power quality problems affecting industrial and commercial customers. They are particularly troublesome Since they occur randomly and are difficult to predict.

Voltage sags are normally associated with system faults on the distribution system, sudden increase in system loads, lightning strikes or starting of large load like induction motors. It is not possible to eliminate faults on a system. One of the most common causes of faults occurring on high-voltage transmission systems is a lightning strike. When there is a fault caused by a lightning strike, the voltage can sag to 50% of the standard range and can last from four to seven cycles. Most loads will be tripped off when encounter this type of voltage level. Possible effect of voltage sags would be system shutdown or reduce efficiency and life span of electrical equipment, particularly motors. 

Equipment sensitivity to voltage sag occurs randomly and has become the most serious power quality problem affecting many industries and commercial customers presently. An industrial monitoring program determined an 87% of voltage disturbances could be associated to voltage sags. Most of the faults on the utility transmission and distribution system are single line-to-ground faults (SLGF). 

5.1.2   Swell

A swell (also known as momentary overvoltage) is an increase in rms voltage or current at the power frequency to between 1.1 and 1.8 pu for durations from 0.5 cycle to 1 min. Swells are commonly caused by system fault conditions, switching off a large load or energizing a large capacitor bank. A swell can occur during a single line-to-ground fault (SLGF) with a temporary voltage rise on the unfaulted phases. They are not as common as voltage sags and are characterized also by both the magnitude and duration. During a fault condition, the severity of a voltage swell is very much dependent on the system impedance, location of the fault and grounding. The effect of this type of disturbance would be hardware failure in the equipment due to overheating. 

5.1.3   Interruption 
An interruption occurs when there is a reduction of the supply voltage or load current to less than 0.1 pu for duration not exceeding 1 min. Possible causes would be circuit breakers responding to overload, lightning and faults. Interruptions are the result of equipment failures, power system faults and control malfunctions. They are characterized by their duration as the voltage magnitude is always less than 10% of the nominal. The duration of an interruption can be irregular when due to equipment malfunctions or loose connections. The duration of an interruption due to a fault on the utility system is determined by the utility protective devices operating time. 

5.2   Long-Duration Voltage Variations 
Long-duration variations can be either overvoltages or undervoltages. They contain root-mean-square (rms) deviations at power frequencies for a period of time longer than 1 min. They are usually not caused by system faults but system switching operations and load variations on the system. 

5.2.1  Overvoltage 
An overvoltage is defined as an increase in the rms ac voltage greater than 110% at the power frequency for duration longer than 1 min. Overvoltages can be the result of switching off a large load, energizing a capacitor bank or incorrect tap settings on transformers. These occur mainly because either the voltage controls are inadequate or the system is too weak for voltage regulation. Possible effect could be hardware failure in the equipment due to overheating. 

5.2.2  Undervoltage 
An undervoltage (also known as brownout) is defined as a decrease in the rms ac voltage to less than 90% at the power frequency for a period of time greater than 1 min. Undervoltage is the result of switching on a load, a capacitor bank switching off or overloaded circuits. Possible effect include system shutdown.  Most electronic controls are very sensitive as compared to electromechanical devices, which tend to be more tolerant. 

5.3   Transients 
Transients can be classified into two categories, namely, impulsive and oscillatory. These terms reflect the wave shape of a current or voltage transient. 

5.3.1   Impulsive Transient 
An impulsive transient is defined as a sudden, non-power frequency change in the steady-state condition of voltage, current, or both, which is unidirectional in polarity (either positive or negative). Impulsive transients are usually measured by their rise and decay times and also their main frequency. Lightning is the most common cause of impulsive transients. The shape of impulsive transients can be changed quickly by circuit components and may have different characteristics when viewed from different parts of the power system when high frequencies are involved. Impulsive transients can even stimulate the natural frequency of power system circuits and produce oscillatory transients. 

5.3.2    Oscillatory Transient 
An oscillatory transient describes as a sudden, non-power frequency change in the steady-state condition of voltage, current, or both, which includes positive and negative polarity values. It consists of a voltage or current whose instantaneous value changes polarity rapidly. They are characterized by its duration, magnitude and main frequency. A back-to-back capacitor energization result in oscillatory transient currents is termed a medium frequency transient. Medium frequency transients can also be the result of a system response to an impulsive transient. Depending on the type of loads, worst case could cause voltage spikes that break insulation somewhere in the system. 

Capacitor switching, which associated with transient, is a daily utility operation to correct the power factor. Many heavy industrial loads such as induction motors and furnaces operate at low power factor. Heavy inductive loads cause excess current to flow in the lines, which increase losses. The effects include equipment damage or failure, process equipment shutdown and computer network problems. 

Installation of capacitor banks can save energy and improve on the system security. A reduction in power loss and an improved voltage profile can be achieved when capacitors are dynamically controlled to changes in the feeder’s load. These benefits depend on how capacitors are sized, placed and in controlled so that savings are maximized. 

In general, the total capacity of capacitor banks is approximately 50% of the total generating capacity in a typical power distribution system. The factors that affect the transient magnitude and characteristics are source strength, transmission lines, other transmission system capacitor banks and switching devices. Pre-insertion resistors and synchronous closing are some of the techniques that involved in the reduction of capacitor switching transients. 

The capacitor voltage is not possible to change instantaneously when energization of a capacitor bank occurs. This results in a sudden drop of system voltage towards zero, followed by a fast voltage overshoot and finally an oscillating transient voltage imposed on the 50Hz waveform. Depending on the instantaneous system voltage at the moment of switching, the peak voltage magnitude can reach two times the normal system peak voltage under severe conditions. Typical distribution system overvoltages due to capacitor switching range from 1.1 - 1.6 pu with transient frequency ranging from 300 – 1 kHz. 

Oscillatory transients with frequencies less than 300 Hz can also be found on the distribution system. They are associated with ferroresonance and transformer energization. Some common methods to limit transient overvoltages on the DC bus of sensitive equipments are: 

· Arrange a reactor in series with AC input terminal. 

· Use of static var compensators (SVCs) in the distribution systems. 

5.4   Voltage Imbalance 
Voltage imbalance (or unbalance) is a condition in which the maximum deviation from the average of the three-phase voltages or currents, divided by the average of the three-phase voltages or currents, expressed in percentage. Voltage imbalance can be the result of blown fuses in one phase of a three-phase capacitor bank. Severe voltage imbalance greater than 5% can cause damage to sensitive equipments. 

5.5  Waveform Distortion 

Waveform distortion is a condition whereby a steady-state deviates from an ideal sine wave of power frequency characterized by the main frequency of the deviation. There are generally five types of waveform distortion, namely, dc offset, harmonics, interharmonics, notching and noise. 

5.5.1   DC Offset 
DC offset is the presence of a dc current or voltage in an ac power system. This can occur due to the effect of half-wave rectification. Direct current found in alternating current networks can have a harmful effect. This can cause additional heating and destroy the transformer. 

5.5.2   Harmonic 
Harmonics are a growing problem for both electricity suppliers and users. A harmonic is defined as a sinusoidal component of a periodic wave or quantity having a frequency that is an integral multiple of the fundamental frequency usually 50Hz or 60Hz. Harmonic refers to both current and voltage harmonics. Harmonic voltages occur as a result of current harmonics, which are created by electronic loads. These nonlinear loads will draw a distorted current waveform from the supply system. The amount of current distortion is dependent upon the kVA rating of the load, the types of load and the fault level of the power system at the point where the load is connected. 

Industrial loads like electric arc furnaces, and discharge lighting can cause harmonic distortion. The effect of harmonics in the power system includes the corruption and loss of data, overheating or damage to sensitive equipment and overloading of capacitor banks. The high frequency harmonics may also cause interference to nearby telecommunication system. 

Fourier analysis can be used to describe distortion in terms of fundamental frequency and harmonic components from a given distorted periodic waveform. By using this technique, we can consider each component of the distorted wave separately and apply superposition.  Using the Fourier series expansion, we can represent a distorted periodic waveshape by its fundamental and harmonic: It is also common to use a single quantity, the Total Harmonic Distortion (THD) as a measure of the effective value of harmonic distortion.  The development of Current Distortion Limits is to: 

· Reduce the harmonic injection from each single consumer so that they will not cause unacceptable voltage distortion levels for normal system characteristics. 

· Restrict the overall harmonic distortion of the system voltage supplied by the utility. 

The harmonic distortion caused by each single consumer should be limited to an acceptable level and the whole system should be operated without existing harmonic distortion. The harmonic distortion limits recommended here provide the maximum allowable current distortion for a consumer. 

5.5.3   Interharmonics 
Interharmonics are defined as voltages or currents having frequency components that are not integer multiples of the frequency at which the supply system is designed to operate. The causes include induction motors, static frequency converters and arcing devices. The effects of interharmonics are not well known. 

5.5.4  Notching 
A periodic voltage disturbance caused by normal operation of power electronics devices when current is commutated from one phase to another is termed notching. Notching tends to occur continuously and can be characterized through the harmonic spectrum of the affected voltage. The frequency components can be quite high and may not be able to describe with measurement equipment used for harmonic analysis. 

5.5.5   Noise 
Noise is unwanted distortion of the electrical power signals with high frequency waveform superimposed on the fundamental. Noise is a common source by electromagnetic interference (EMI) or radio frequency interference (RFI), power electronic devices, switching power supplies and control circuits. Noise disturbs electronic devices such as microcomputer and programmable controllers. Use of filters and isolation transformers can usually solve the problem. 

5.6   Voltage Fluctuation 
Voltage fluctuation is defined as the random variations of the voltage envelope where the magnitude does not exceed the voltage ranges of 0.9 to 1.1 pu. Flicker usually associates with loads that display continuous variations in the load current magnitude causing voltage variations. The flicker signal is measured by its rms magnitude expressed as a percent of the fundamental whereas voltage flicker is measured with respect to the sensitivity of human eye. It is possible for lamp to flicker if the magnitudes are as low as 0.5% and the frequencies are in the range of 6 to 8 Hz. One common cause of voltage fluctuations on utility transmission and distribution system is the arc furnace. 

5.7   Power Frequency Variations 
Any deviation of the power system fundamental frequency from its nominal value (usually 50 or 60 Hz) is defined as power frequency variations. The power system frequency is associated with the rotational speed of the generators supplying the system. The size and duration of the frequency shift depends on the load characteristics and the response of the generation control system to load changes. As the load and generation changes, small variations in frequency occur. 
Frequency variations can be the cause of faults on power transmission system, large load being disconnected or a large source of generation going off-line. Frequency variations usually occur for loads that are supplied by a generator isolated from the utility system. The response to sudden load changes may not be sufficient to adjust within the narrow bandwidth required by frequency sensitive equipment. Possible effect could result in data loss, system crashes and equipment damage. 

6.   Reactive Power Problems
Reactive power problems usually occur at the interconnection points of different systems or now in the deregulated market between different owners of transmission or distribution networks, reactive power generators and consumers. As reactive power is a local product its value to system security and voltage control very much depends on the location in the system.

The existence of embedded generation can release capacity in a distribution or other network to which it is connected. And any generation embedded on that network reduces the likelihood of overloading and loss of supply, so improving the reliability of the network.

Wind power stations is a common example of embedded generation. A specific character of those power stations is that while generating the active power they consume the reactive one. Combined with the generation level that varies with the weather conditions, this causes voltage problems at the interconnection points and the installment of compensation devices is required.  
6.1 Reactive Power Sources

Reactive power is produced or absorbed by all major components of a power system:
· Generators;

· Power transfer components;

· Loads;

· Reactive power compensation devices.
· Power factor Corrections
6.1.1 Generators

Electric power generators are installed to supply active power. Additionally a generator is supporting the voltage, producing reactive power when over-excited and absorbing reactive power when under-excited. Reactive power is continuously controllable. The ability of a generator to provide reactive support depends on its real-power production. Like most electric equipment, generators are limited by their current-carrying capability.

Reactive power production is depended on the field heating limit and absorption on the core end-heating limit of the generator. Active power output limit is limited by armature heating. Control over the reactive output and the terminal voltage of the generator is provided by adjusting the DC current in the generator’s rotating field. Control can be automatic, continuous, and fast. The inherent characteristics of the generator help maintain system voltage. At any given field setting, the generator has a specific terminal voltage it is attempting to hold. If the system voltage declines, the generator will inject reactive power into the power system, tending to raise system voltage. If the system voltage rises, the reactive output of the generator will drop, and ultimately reactive power will flow into the generator, tending to lower system voltage. The voltage regulator will accentuate this behavior by driving the field current in the appropriate direction to obtain the desired system voltage.

6.1.2 Power transfer components

The major power transfer components are transformers, overhead lines and underground

cables. HVDC converter stations can also be treated as power transfer components.

6.1.2.1 Transformers
Transformers provide the capability to raise alternating-current generation voltages to levels that make long-distance power transfers practical and then lowering voltages back to levels that can be distributed and used. The ratio of the number of turns in the primary to the number of turns in the secondary coil determines the ratio of the primary voltage to the secondary voltage. By tapping the primary or secondary coil at various points, the ratio between the primary and secondary voltage can be adjusted. Transformer taps can be either fixed or adjustable under load through the use of a load-tap changer (LTC). Tap capability is selected for each application during transformer design. Fixed or variable taps often provide ±10% voltage selection, with fixed taps typically in 5 steps and variable taps in 32 steps. Transformer-tap changers can be used for voltage control, but the control differs from that provided by reactive sources. Transformer taps can force voltage up (or down) on one side of a transformer, but it is at the expense of reducing (or raising) the voltage on the other side. The reactive power required to raise (or lower) voltage on a bus is forced to flow through the transformer from the bus on the other side. The reactive power consumption of a transformer at rated current is within the range 0.05 to 0.2 p.u. based on the transformer ratings. Fixed taps are useful when compensating for load growth and other long-term shifts in system use. LTCs are used for more-rapid adjustments, such as compensating for the voltage fluctuations associated with the daily load cycle. While LTCs could potentially provide rapid voltage control, their performance is normally intentionally degraded. With an LTC, tap changing is accomplished by opening and closing contacts within the transformer’s tapchanging mechanism.

6.1.2.2 Transmission lines and cables
Transmission lines and cables generate and consume reactive power at the same time.

The reactive power generation is almost constant, because the voltage of the line is usually constant, and the line’s reactive power consumption depends on the current or load connected to the line that is variable. So at the heavy load conditions transmission lines consume reactive power, decreasing the line voltage, and in the low load conditions – generate, increasing line voltage. The case when line’s reactive power production is equal to consumption is called natural loading.

6.1.2.3 HVDC converters
Thyristor-based HVDC converters always consume reactive power when in operation. The reactive power consumption of the HVDC converter/inverter is 50-60 % of the active power converted. The reactive power requirements of the converter and system have to be met by providing appropriate reactive power in the station. For those reason reactive power compensations devices are used together with reactive power control from the ac side.

6.1.3  Loads

Voltage stability is closely related to load characteristics. The reactive power consumption of the load has a great impact on voltage profile at the bus. The response of loads to voltage changes occurring over many minutes can affect voltage stability. For transient voltage stability the dynamic characteristics of loads such as induction motors are critical. Some typical reactive power consuming loads examples are given below.

6.1.3.1 Induction motors
About 60 % of electricity consumption goes to power motors and induction motors take nearly 90 % of total motor energy depending on industry and other factors. The steady-state active power drawn by motors is fairly independent of voltage until the point of stalling. The reactive power of the motor is more sensitive to voltage levels. As voltage drops the eactive power will decrease first, but then increase as the voltage drops further.

6.1.3.2 Induction generators
Induction generators as reactive power load became actual with the wind power station expansion into electricity sector. Wind plants are equipped with induction generators, which require a significant amount of reactive power. Part of the requirement is usually supplied by local power factor correction capacitors, connected at the terminal of each turbine. The rest is supplied from the network, which can lead to low voltages and increased losses.

6.1.3.3 Discharged lightning
About one-third of commercial load is lightning – largely fluorescent. Fluorescent and other discharged lightning has a voltage sensitivity Pv in the range 1-1.3 and Qv in the range 3- 4.5. At voltages between 65-80 % of nominal they will extinguish, but restart when voltage recovers.

6.1.3.4 Constant energy loads
Loads such as space heating, water heating, industrial process heating and air conditioning are controlled by thermostats, causing the loads to be constant energy in the time scale of minutes. Heating loads are especially important during wintertime, when system load is large and any supply voltage drop causes an increase in load current, that makes situation even worse.

6.1.3.5 Arc furnaces
Arc furnaces are a unique representation of problems with voltage stability, power factor correction and harmonic filtering. Rapid, large and erratic variations in furnace current cause voltage disturbances for supply utility and nuisance to neighboring customers. So the

problem of voltage stabilization and reactive power control is usually solved by connecting

the furnace to a higher network voltage, installing synchronous condensers and other fast

responding reactive power generating units.

6.1.4  Reactive Power compensation devices

6.1.4.1 Synchronous condensers
Every synchronous machine (motor or generator) has the reactive power capabilities the same as synchronous generators. Synchronous machines that are designed exclusively to provide reactive support are called synchronous condensers. Synchronous condensers have all of the response speed and controllability advantages of generators without the need to construct the rest of the power plant (e.g., fuel-handling equipment and boilers). Because they are rotating machines with moving parts and auxiliary systems, they require significantly more maintenance than static compensators. They also consume real power equal to about 3% of the machine’s reactive-power rating. Synchronous condensers are used in transmission systems: at the receiving end of long transmissions, in important substations and in conjunction with HVDC converter stations. 
Small synchronous condensers have also been used in high-power industrial networks to increase the short circuit power. The reactive power output is continuously controllable. The response time with closedloop voltage control is from a few seconds and up, depending on different factors.

In recent years the synchronous condensers have been practically ruled out by the thyristor controlled static VAR compensators, because those are much more cheaper and have regulating characteristics similar to synchronous condensers.

6.1.4.2 Static VAR compensators
An SVC combines conventional capacitors and inductors with fast switching capability. Switching takes place in the sub cycle timeframe (i.e., in less than 1/50 of a second), providing a continuous range of control. The range can be designed to span from absorbing to generating reactive power. Advantages include fast, precise regulation of voltage and unrestricted, largely transient-free, capacitor bank switching. Voltage is regulated according to a slope characteristic. 
Static VAR compensator could be made up from:

1. TCR (thyristor controlled reactor);

2. TSC (thyristor switched capacitor);

3. TSR (thyristor switched reactor);

4. FC (fixed capacitor);

6.1.4.3 Harmonic filter
Because SVCs use capacitors they suffer from the same degradation in reactive capability as voltage drops. They also do not have the short-term overload capability of generators and synchronous condensers. SVC applications usually require harmonic filters to reduce the amount of harmonics injected into the power system by the thyristor switching. SVCs provide direct control of voltage; this is very valuable when there is little generation in the load area. The remaining capacitive capability of an SVC is a good indication of proximity to voltage instability. SVCs provide rapid control of temporary overvoltages. But on the other hand SVCs have limited overload capability, because SVC is a capacitor bank at its boost limit. The critical or collapse voltage becomes the SVC regulated voltage and instability usually occurs once an SVC reaches its boost limit. SVCs are expensive; shunt capacitor banks should first be used to allow unity power factor operation of nearby generators.

6.1.4.4 Static synchronous compensator (STATCOM)
The STATCOM is a solid-state shunt device that generates or absorbs reactive power and is one member of a family of devices known as flexible AC transmission system (FACTS) devices. The STATCOM is similar to the SVC in response speed, control capabilities, and the use of power electronics. Rather than using conventional capacitors and inductors combined with thyristors, the STATCOM uses self-commutated power electronics to synthesize the reactive power output. Consequently, output capability is generally symmetric, providing as much capability for production as absorption. The solid-state nature of the STATCOM means that, similar to the SVC, the controls can be designed to provide very fast and effective voltage control.

While not having the short-term overload capability of generators and synchronous condensers, STATCOM capacity does not suffer as seriously as SVCs and capacitors do from degraded voltage. STATCOMs are current limited so their MVAR capability responds linearly to voltage as opposed to the voltage-squared relationship of SVCs and capacitors. This attribute greatly increases the usefulness of STATCOMs in preventing voltage collapse.

6.1.4.5 Series capacitors and reactors
Series capacitors compensation is usually applied for long transmission lines and transient stability improvement. Series compensation reduces net transmission line inductive reactance. The reactive generation I2XC compensates for the reactive consumption I2X of the transmission line. Series capacitor reactive generation increases with the current squared, thus generating reactive power when it is most needed. This is a self-regulating nature of series capacitors. At light loads series capacitors have little effect.

6.1.4.6 Shunt capacitors
The primary purposes of transmission system shunt compensation near load areas are

voltage control and load stabilization. Mechanically switched shunt capacitor banks are

installed at major substations in load areas for producing reactive power and keeping voltage within required limits. For voltage stability shunt capacitor banks are very useful in allowing nearby generators to operate near unity power factor. This maximizes fast acting reactive reserve. Compared to SVCs, mechanically switched capacitor banks have the advantage of much lower cost. Switching speeds can be quite fast. Current limiting reactors are used to minimize switching transients.

There are several disadvantages to mechanically switched capacitors. For voltage emergencies the shortcoming of shunt capacitor banks is that the reactive power output drops with the voltage squared. For transient voltage instability the switching may not be fast enough to prevent induction motor stalling. Precise and rapid control of voltage is not possible. Like inductors, capacitor banks are discrete devices, but they are often configured with several steps to provide a limited amount of variable control. If voltage collapse results in a system, the stable parts of the system may experience damaging overvoltages immediately following separation.

6.1.4.7 Shunt reactors
Shunt reactors are mainly used to keep the voltage down, by absorbing the reactive power, in the case of light load and load rejection, and to compensate the capacitive load of the line.

6.1.5  Why Power Factor Correction
· Increased source efficiency

- lower losses on source impedance

- lower voltage distortion (cross-coupling)

- higher power available from a given source
· Reduced low-frequency harmonic pollution
· Compliance with limiting standards (IEC 555-2, IEEE 519 etc.)
6.1.5.1    Power Factor Correction Techniques
· PASSIVE METHODS: LC filters

· Power factor not very high

· Bulky components

· High reliability

· Suitable for very small or high power levels

· ACTIVE METHODS: high-frequency converters

· High power factor (approaching unity)

· Possibility to introduce a high-frequency insulating transformer layout dependent high-frequency harmonics generation (EMI problems)

· Suitable for small and medium power levels
7.  Software
In most cases, specialized software tools make use of intelligent techniques to computerize the power quality evaluations for improved accuracy and efficiency, as manual analysis may be too difficult to carry out due to lack of time and special knowledge. There have been an increasing number of simulation tools suitable for transient analysis in the last few years. Besides the well-known EMTP and its variants ATP, MATLAB, and the PSCAD / EMTDC.

In this course, both the MATLAB and PSCAD/EMTDC software have been used for analyzing power systems disturbances. 
8.     Digital Simulation Models
Grid electricity is generally distributed as three phase balanced voltage waveforms forming the common 3-phase sinusoidal AC system. One of the characteristics of the AC system is its sinusoidal voltage waveforms, which must always remain as close as possible to that of a pure sine-wave. If it is distorted beyond certain acceptable limits, as is often the case on power source networks comprising nonlinear type loads, the supply waveform must be cleaned and corrected. The distorted waveform is usually composed of a number of dominant sine waves of different harmonic frequencies, including the fundamental one at the 60Hz power frequency, referred as the fundamental frequency, and the rest is referred to as the “integral harmonic ripple component” with frequencies which are multiple of that of the fundamental. Harmonic effective quantities are generally expressed in terms of their RMS-value since the heating or loss effect depends on this total sum squared value of the distorted waveform. 
8.1   System Models
[image: image34.emf]Cn 4

C 3

B 2

A 1

A B

C

+

-

S1

g

1

2

S 2

g

1

2

Rf

Lf

Cf

AB

C

AB

C

s2

2

s1

1

Figure 8.1 depicts the single line diagram of radial utilization system feeding a nonlinear type load. The load bus is connected to the switched/modulated Smart Power Filter (SMPF). SMPF can be used to improve electric supply power quality by reducing harmonic content in supply current by minimizing waveform distortion, notching and voltage fluctuations (swell, sag). Rs and Ls represent the equivalent source transformer feeder resistance and inductance. 
[image: image16.wmf]S

V

 and 
[image: image17.wmf]L

V

 represent the supply and load voltage respectively.

[image: image35.png]e
VoG |y
O

W







8.1.1 CASES # 1 TO # 5

CASE # 1

Case # 1 addresses the power quality enhancement scheme using modulated power filter compensator. The modulated power filter is developed by Dr. Sharaf. The use of the switched modulated power filter compensator is to enhance power quality in low voltage distribution systems under unbalanced and fault conditions. The simulation results are shown in Appendix A and are done with and without the modulated power compensating filter. The software used in this case is the Matlab/Simulink.
The complete system model is depicted in Appendix A. The Modulated power filter is controlled by a dynamic tri-loop controller. The purpose of this dynamic controller is to minimize switching transients, maximize power/energy utilization and to improve power factor under unbalanced load and fault conditions. The major components of the AC system are: Three phase-four wire AC power supplies; Novel Modulated power Filter; Tri -loop dynamic error driven error controller and Single phase load. 

CASE # 2
Case # 2 addresses another power quality enhancement scheme also using modulated power filter compensator. The modulated power filter is developed by Dr. Sharaf.  This case presents a novel dynamic voltage regulator Power filter and capacitor correction compensator   scheme to enhance power utilization and improve power quality in low voltage distribution systems under the nonlinear load conditions. The modulated power filter is controlled by a dynamic tri-loop error driven PID controller. The purpose of this dynamic hybrid Tri-functional compensator is to minimize feeder switching transients, maximize power/energy utilization and to improve power factor under unbalanced load and fault conditions. The functional MATLAB/SIMULINK model of a radial distribution system with the proposed dynamic hybrid reactive power compensation scheme is presented as shown in Appendix B. 

CASE # 3
Case # 3 illustrates the use of a STATCOM to provide active filtering for the ac side of a 6-pulse converter system. The Active filter is connected through a 20 kVA, Y-Y transformer to a 200 V, 50 Hz, 3-Phase bus, with a 6-pulse converter load

The simulation results are shown in Appendix C and are done with and without the compensating filter. Graphs show clearly the difference in harmonic contents in the supply current and demonstrate the Power quality improvement and the efficiency of the compensating filter. The software used in this case is the PSCAD.
CASE # 4
Case # 4 illustrates the power quality problem of Tingle Voltage; the problem was that farm animals, during winter months, were experiencing a "tingle voltage", due to suspected poor grounding on the local ground grid. 

By using PSCAD, the local system is simulated and determined that the grounding problem was at least partially related to ground rod resistance. During the winter months, the ground conductivity is poor, resulting in a poor connection between the ground rods and earth. 
The simulation results are shown in Appendix D and are done by varying the ground resistor. Graphs show clearly the difference in voltage affecting the cows. By varying the ground resistance, the voltage varies and affects the cows. 
CASE # 5
Case # 5 illustrates the use of a 12-Pulse STATCOM for Reactive power control. The STATCOM is a solid-state shunt device that generates or absorbs reactive power and is one member of a family of devices known as flexible AC transmission system (FACTS) devices. The STATCOM is similar to the SVC in response speed, control capabilities, and the use of power electronics. Rather than using conventional capacitors and inductors combined with thyristors, the STATCOM uses self-commutated power electronics to synthesize the reactive power output. Consequently, output capability is generally symmetric, providing as much capability for production as absorption. The solid-state nature of the STATCOM means that, similar to the SVC, the controls can be designed to provide very fast and effective voltage control.

The simulation results are shown in Appendix E and the control is designed to provide very fast and effective voltage control. The software used in this case is the PSCAD.
References

[1] A. M. Sharaf and M. A. Habli, “Demand Side Management and Energy Conservation Using Switched Capacitor Compensation”, Proceedings of the International Conference ICCCP01 Muscat, Oman, Feb 2001.

[2] A. M. Sharaf, S Abu-Azab “Power Quality Enhancement of Time Dependent Interharmonic Loads “ Proceedings of the Nonth International IEEE Conference on Harmonics and Quality of Power ICHPS’2000, Orlando, FL, October 2000.

[3] A.M. Sharaf, Caixia Guo, and Hong Huang. “A novel smart compensation for energy/power quality enhancement of nonlinear loads”, Proceedings of the 1997 Canadian Conference on Electrical and Computer Engineering, CCECE, May 25-28, 1997, St. John’s, Newfoundland, Canada.

[4] W. Mack Grady, “Harmonics and how they relate to power factor”, Proceedings of the EPRI Power Quality Issues and Opportunities Conference, San Diego, CA, November 1993.

[5] A.M. Sharaf, Pierre Kreidi, ”Dynamic compensation using switched/modulated power filters, ” Proceedings of the IEEE     Canadian Conference on Electrical and Computer Engineering CCECE 2002, Winnipeg, Manitoba, Canada, May 12-15, 2002

[6] A.M. Sharaf, Pierre Kreidi, ”Power quality enhancement and   harmonic   reduction    using    dynamic power filters,” 7th International Conference on Modeling and Simulation of Electric Machines, Converters and Systems. ELECTRIMACS 2002.  Montreal, Quebec, Canada, August 18-21, 2002.

[7] A.M. Sharaf, Pierre Kreidi, ”Power quality enhancement and harmonic compensation scheme for asymmetrical nonlinear loads”, 10th International Power Electronics and Motion Control Conference. EPE-PEMC 2002 Cavtat & Dubrovnik, Croatia, September 9-11, 2002.

[8] A.M. Sharaf, Pierre Kreidi, ”Power quality enhancement using a unified compensator and switched filter”, International Conference on Renewable Energy and Power Quality-ICREPQ’2003, Vigo-Spain, April 9-11, 2003

[9] A.M. Sharaf, Pierre Kreidi, ”Power quality enhancement using a unified switched capacitor compensator,” Proceedings of the IEEE Canadian Conference on Electrical and Computer Engineering CCECE 2003, Montreal, Quebec, Canada, May 4-7, 2003

[10] A.M. Sharaf, Wei Wu, “A Novel Power Quality Enhancement Scheme In Low Volatge Distribution System Using Modulated Power Filter Compensator”.
[11] A.M. Sharaf,  Ting Zhang, “Novel Power Quality Enhancement  Scheme Using Modulated Power Filter Compensator”
[12] Valery Knyazkin, “Technical Report – The Oxelösund Case Study”, A-EES-0010, August 2000.

[13] MC. Ryan et al., “Power Quality reference guide”, Ontario Hydro Publications. 2nd edition, 1990.

[14] RC Dugan, M.F. McGranaghan, H.W. Beaty, “Electrical Power Systems Quality”, McGraw Hill, 1996, ISBN 0-07-018031-8.

[15] Peter Axelberg et al., “Current and Emerging Trends in IEC Standards and Their Implications for Power quality Measurement Systems”, Electrical Distribution and Transmission PTY LTD Publications, 2001.

[16] Electrical Business Magazine, December 2001. The Authoritative voice of Canada’s electrical industry. Kerwil Publications.

[17] EPRI and CEIDS Team, “The Power Quality Implications of Conservation Voltage Reduction”, EPRI Publications – PQ Commentary Number 4, December 2001.

[18] K Srinivasan, R. Jutras, T.D. Nguyen, “Sharing steady state power quality deterioration  between customer and utility sides”, Power Quality Applications 1997 Europe, Stockholm, June1997.

[19] Owyong Leng, “Simulating Power Quality Problems”, BS Thesis, University of Queensland, Australia, 2001.

[20] National Electrical Code Internet Connection, “Case Studies”, http://www.neccode.com/studies/harmonic.htm.

[21] Pierre Kreidi “Electric Power Quality, Harmonic Reduction and Power/Energy Saving Using Modulated Power Filters and Capacitor Compensators” Thesis , UNB 2003.
[image: image36.emf]0 0.1 0.2 0.3 0.4 0.5

-0.5

0

0.5

power factor @ phase A

0 0.1 0.2 0.3 0.4 0.5

0

0.5

1

power factor @ phase B

0 0.1 0.2 0.3 0.4 0.5

-0.5

0

0.5

1

power factor @ phase C

Time (s)

[image: image37.emf]0 0.05 0.1 0.15 0.2 0.25 0.3 0.35

0.6

0.8

1

power factor @ phase A

0 0.05 0.1 0.15 0.2 0.25 0.3 0.35

0.5

1

power factor @ phase B

0 0.05 0.1 0.15 0.2 0.25 0.3 0.35

0.6

0.8

1

power factor @ phase C

Time (s)


[image: image38.emf]0 0.1 0.2 0.3 0.36

0

0.5

1

1.5

Load Current (rms)/pu @ phase A

0 0.1 0.2 0.3 0.36

0

0.5

1

Load Current (rms)/pu @ phase B

0 0.1 0.2 0.3 0.36

0

0.5

1

Load Current (rms)/pu @ phase C

Time (s)

[image: image39.emf]0 0.5 1 1.5 2 2.5 3 3.5

x 10

4

0

0.5

1

Load Current (rms)/pu @ phase A

0 0.5 1 1.5 2 2.5 3 3.5

x 10

4

0

0.2

0.4

Load Current (rms)/pu @ phase B

0 0.5 1 1.5 2 2.5 3 3.5

x 10

4

0

0.2

0.4

Load Current (rms)/pu @ phase C

Time(s)


[image: image40.emf]0 0.1 0.2 0.3 0.4 0.5

0

0.5

1

Load Voltage (rms)/pu @ phase A

0 0.1 0.2 0.3 0.4 0.5

0

0.5

1

Load Voltage (rms)/pu @ phase C

0 0.1 0.2 0.3 0.4 0.5

0

0.5

1

Load Voltage (rms)/pu @ phase B

Time (s)



[image: image41.emf]0 0.5 1 1.5 2 2.5 3 3.5

x 10

4

0

0.5

1

1.5

Load Voltage (rms)/pu @ phase A

0 0.5 1 1.5 2 2.5 3 3.5

x 10

4

0

0.5

1

1.5

Load Voltage (rms)/pu @ phase B

0 0.5 1 1.5 2 2.5 3 3.5

x 10

4

0

0.5

1

Load Voltage (rms)/pu @ phase C

Time (s)


[image: image42.emf]0   0.1 0.2 0.3 0.4 0.5

0

0.1

0.2

Power/pu @ phase A

0 0.1 0.2 0.3 0.4 0.5

0

0.1

0.2

Power/pu @ phase B

0 0.1 0.2 0.3 0.4 0.5

0

0.1

0.2

Power/pu @ phase C

Time (s)


[image: image43.emf]0 0.05 0.1 0.15 0.2 0.25 0.3 0.35

0

0.1

0.2

Power/pu @ phase A

0 0.05 0.1 0.15 0.2 0.25 0.3 0.35

0

0.1

0.2

Power/pu @ phase B

0 0.05 0.1 0.15 0.02 0.25 0.3 0.35

0

0.1

0.2

Power/pu @ phase C

Time (s)


[image: image44.emf]0.15 0.2 0.25

0

0.2

0.4

0.6

0.8

1

S1

0.15 0.2 0.25

0

0.2

0.4

0.6

0.8

1

S2

Time(s)


[image: image45.emf]138kv

25kv

Transmission line

25kv 2km

powergui

Continuous

load4 1MVA@PF=0.8

Voltage Measurement 6

v

+

-

v

+

-

v

+

-

v

+

-

v

+

-

v

+

-

v

+

-

V6

Scope

N.L.Load

In

Measurement6

I

V

Measurement5

I

V

Measurement4

I

V

Measurement3

I

V

Measurement2

I

V

Measurement1

I

V

Load6 1MVA@PF=0.8

Linear Transformer

1 2

g1

2

g

1

2

Harmonic Analysis

I

[S2]

[S1]

IL

[PF]

[IL]

[S2]

[S1]

i

+

-

i

+

-

i

+

-

i

+

-

i

+

-

i

+

-

i

+

-

i

+

-

Controller

VL

IL

PF

PWM1

PWM2

 Load5 1MVA@PF=0.8

 Load3 1.5MVA@PF=0.8

 Load2 1.5MVA@PF=0.8   Load1 2MVA@PF=0.8


[image: image46.emf]Et

PWM2

2

PWM1

1

rEp

Vrms2

signal

rms

Vrms1

signal

rms

V1 ref1

0.98

V1 ref

1

Transfer Fcn2

1

0.02s+1

Transfer Fcn1

1

0.02s+1

Saturation

PWM Generator

Signal(s)

Pulses

PWM

Gama V

1

Gama P

0.5

Gain1

-

K-

Gain

K-

Ev

Et

Epf

PID

Delay2

PF

3

IL

2

VL

1

[image: image47.emf]In

1

Voltage Measurement 1

v

+

-

Voltage Measurement

v

+

-

V.I

Universal Bridge

g

A

+

-

Terminator

PWM Generator

Signal(s)

Pulses

Measurement7

I

V

Current Measurement 7

i

+

-

25kV/0.8kV

1 2

[image: image48.png]Buzn

G
20wz

&

»fr z
e L
et Switht

ALe

Busnet

L;ﬁ:ﬁ!

el Switehz




 

[image: image49.png]1200

1000

Eul

600

am

m

10

V_ren

016

018

02 02 02t 0%

028





[image: image50.png]5000

4000

000

2000

1000}

1400

1200
1000
a0
&0
an

006

3

i i i
01 01z 01 016 o1 02



[image: image51.png]10
.

001

Ev6

002 003 004 005 005 007

008




[image: image52.emf]
[image: image53.emf]
[image: image54.emf]
























[image: image18.emf]
[image: image19.emf]
[image: image20.emf]


[image: image21.emf]


[image: image22.emf]


[image: image23.emf]



[image: image24.emf]
[image: image25.emf]


[image: image26.emf]


[image: image27.emf]


[image: image28.emf]


[image: image29.emf]
CASE # 3





WITH COMPENSATING FILTER





WITHOUT COMPENSATING FILTER





(4.1)





(4.2)





Figure 1.1: The Power Quality Diagram





�EMBED Visio.Drawing.5���





� EMBED Visio.Drawing.5  ���





Figure 8.1: Single Line Diagram of Radial Utilization System





CASE # 3





CASE # 3





CASE # 3





CASE # 3





CASE # 3





CASE # 4





CASE # 4





CASE # 5





CASE # 5





CASE # 5





CASE # 5





APPENDIX ‘C’





APPENDIX ‘C’





APPENDIX ‘D’





APPENDIX ‘D’





APPENDIX ‘E’





APPENDIX ‘E’





APPENDIX ‘A’





CASE # 1





�





�





�





�





�





�





Load Power Factor   








Without Filter Compensation








With Filter Compensation








�





�





Load Current





�





�





Load Voltage





�





�





Power





�





Compensator S1 and S2





APPENDIX ‘B’





CASE # 2





�





�





�





With Filter Compensation








Without Filter Compensation








�





�





�





Current and voltage waveforms of the nonlinear load without and with compensation








�





�





Voltage waveforms of the linear load without and with compensation





�





�





Voltage waveforms and P-Q profile without and with compensation








Converter type non-linear loads





Dynamic Tri-loop error driven PID controller





Simulink model of the radial distribution system with the non- linear load





Compensation Switching





Modulated Power Filter Compensator Scheme





Matlab- Simulink functional model of the 3Phase-4 Wire Model





Tri loop dynamic Variable structure-sliding mode control Scheme





Converter type nonlinear load model








Page 2 of 58

_1112377581.unknown

_1112377804.unknown

_1112377903.unknown

_1112378026.unknown

_1112392198.unknown

_1112377933.unknown

_1112377840.unknown

_1102427534.unknown

_1112376756.unknown

_1112377543.unknown

_1112377446.unknown

_1109426395.unknown

_1109437096.vsd
SMPF�

YF(s)�

Nonlinear Load (NLL)�

* Smart-controllers are based on specified control objectives�

Nonlinear
Load
�

N
L
L�

Rs�

Ls�

Vs�

VL�

on/off or
PWM
�

Load Bus�

Converter Type
Arc Type
Dynamic
Cyclical
Ripple
Inrush
Temporal
Motorized on/off�

Utility�

System+Transformer+Feeder�

Electric Equivalent (Plant) Load�

Switched/Modulated Power Filter or Static Capacitor Compensator�

 is �

Control
Signals�

Smart Controller
*�

Vs�

Ps�


_1109345054.vsd
Electrical Grid
Utility�

Loads
Consumers�

Voltage 
Quality�

Current 
Quality�

Power 
Quality�


_1102426540.unknown

_1102427123.unknown

_1083440357.unknown

